## Tool Description
DC-E-WISE (Data Center Energy and Water Information Simulator and Evaluator)
| Version | 2023.V1 | Note: The cooling energy and water use for the systems included in this tool were calculated based on our developed 8760 energy and water analysis based on meteorological year (TMY3) weather data for Phoenix-Sky Harbor International Airport (weather station with location code 722780) from the EnergyPlus weather database.Therefore, this version of the MCDST is currently applicable for data centers in Phoenix, AZ. Its application can be extended to other locations within climate type 2B (ASHRAE's classification).
| Application | Phoenix, AZ
Tool Description
The DC-E-WISE is an excel-based tool that we developed to facilitate the comparison of nine cooling systems based on five main criteria: Energy Use, Onsite Water Use, Total Cooling Water Use, Reliability, and Maintenance. The nine studied cooling systems are: Air-cooled chiller, Air-cooled chiller + Air-side economizer (ASE), Pre-cooled-air-cooled chiller, Pre-cooled-air-cooled chiller + ASE, Water-cooled chiller, Water-cooled chiller + ASE, Water-cooled chiller + Water-side economizer (WSE), Water-cooled chiller + ASE + WSE, and Evaporative cooling system + ASE. The DC-E-WISE tool employs the technique for order preference by similarity to ideal solution (TOPSIS) method to rank the modeled cooling systems. The tool then presents a tabulated list of the ranked cooling systems, which includes energy and water use data, as the result. By utilizing the TOPSIS method, the tool provides a systematic and objective way of comparing and ranking the cooling systems, enabling users to make informed decisions when selecting and optimizing cooling systems for their data centers. The tabulated result provides a concise summary of the ranked cooling systems, allowing users to quickly identify the most efficient and effective options for their specific needs. This tool utilizes modeling data for cooling energy, water use (onsite cooling and humidification), and total cooling water use in DCs located in the greater Phoenix area. The power and water use data, which are model outputs, are normalized based on the modeled IT load (in MW) at the uninterrupted power supply (UPS) output. Therefore, the tool can calculate the total energy and onsite and total cooling water use for a given IT load as entered by the user. Along with overall DC power and water use, the tool provides estimates for key DC metrics including PUE, WUEOnsite, and WUESource.
Disclaimer
The DC-E-WISE was prepared as an account of work sponsored by Salt River Project (SRP).

## User_Interaction
Availability of Cooling System (Percentage of the Year)
50%
100%
100%
100%
100%
100%
100%
100%
100%
#N/A
Note on I3: lkari: Note: Total Cooling Water Use data include both Onsite Water Use and the Water used to generate the cooling power used in the facility.
Run Calculation
Show Results
Print Results
to PDF
User Input Form

## Cooling System Schematics
Cooling Systems Schematics | Cooling Systems Modeling Parameters and Assumptions
Air-Cooled Chiller
Air-Cooled Chiller+ASE
Pre-Cooled Air-Cooled Chiller
Pre-Cooled Air-Cooled Chiller+ASE
Water-Cooled Chiller+ASE
Water-Cooled Chiller
Adiabatic Evaporative Cooling+ASE
Water-Cooled Chiller+ASE+WSE
Water-Cooled Chiller+WSE

## Acknowledgments
Acknowledgments
Development Team | Sponsor
Leila Karimi* (UofA) | Salt River Project (SRP): Arizona electric power and water utility company
Kerri Hickenbottom (UofA)
Reema Shinh (UofA)
Leeann Yacuel (SRP)
Michael Green (SRP)
Jamie Ashby (SRP)
Joseph Degraft-Johnson (SRP)
Advising and Outreach | Contact
Colin Laisure-Pool, Central AZ ASHRAE GAC Chair | *Email: lkarimi@arizona.edu
Matt Renner, Northshore IO Inc | *Phone: (915) 207-0240

## No Airflow Containment
Airflow Type
Configuration | Selected
|  | Parameters Weight Percentage |  |  |  |  | Normalized Performance Values (NPVs) |  |  |  |  | Weighted Normalized Values(WNVs) |  |  |  |  | Ideal Best Value (V-) |  |  |  |  | Ideal Worst Value (V-) |  |  |  |  | Cooling System Availbility (% of the Year)
|  | 30.74 | 13.4573 | 14.0832 | 35.208 | 6.5116
Cooling System | Paramter Unit | Energy Use (MWh/MW IT Load) | Onsite Water Use (acre-ft/MW IT Load) | Total Cooling Water Use (acre-ft/MW IT Load) | Reliability | Maintenance | NPV_Energy | NPV_Onsite Water | NPV_Source Water | NPV_Reliability | NPV_Maintenance | WNV_Energy | WNV_Onsite Water | WNV_Source Water | WNV_Reliability | WNV_Maintenance | V+_Energy | V+_Onsite Water | V+_Source Water | V+_Reliability | V+_Maintenance | V-_Energy | V-_Onsite Water | V-_Source Water | V-_Reliability | V-_Maintenance
Air-Cooled Chiller | Parameter Unit/MW IT Load | 3747.04 | 0.003 | 4.91 | 89 | 81 | 0.45497 | 7.1885e-05 | 0.098216 | 0.35867 | 0.22212 | 0.13986 | 9.6738e-06 | 0.013832 | 0.12628 | 0.014464 | 0.01627 | 9.6738e-06 | 0.012787 | 0.12628 | 0.0073211 | 0.13986 | 0.071844 | 0.073639 | 0.083359 | 0.029106 | 100
Air-Cooled Chiller+ ASE | Parameter Unit/MW IT Load | 2866.7658 | 0.78204 | 4.539 | 83.25 | 100 | 0.34808 | 0.018739 | 0.090794 | 0.3355 | 0.27422 | 0.107 | 0.0025217 | 0.012787 | 0.11812 | 0.017856 | [10 empty] | 100
Pre-Cooled-Air-Cooled Chiller | Parameter Unit/MW IT Load | 3440.87 | 5.968 | 10.477 | 88 | 103 | 0.41779 | 0.143 | 0.20957 | 0.35464 | 0.28245 | 0.12843 | 0.019244 | 0.029515 | 0.12486 | 0.018392 | [10 empty] | 100
Pre-Cooled-Air-Cooled Chiller +ASE | Parameter Unit/MW IT Load | 2560.072 | 6.874 | 10.139 | 82.25 | 122 | 0.31084 | 0.16471 | 0.20281 | 0.33147 | 0.33455 | 0.095553 | 0.022166 | 0.028562 | 0.1167 | 0.021785 | [10 empty] | 100
Water-Cooled Chiller | Parameter Unit/MW IT Load | 2947.35 | 22.28 | 26.14 | 88.5 | 135 | 0.35787 | 0.53387 | 0.52288 | 0.35665 | 0.3702 | 0.11001 | 0.071844 | 0.073639 | 0.12557 | 0.024106 | [10 empty] | 100
Water-Cooled Chiller+ASE | Parameter Unit/MW IT Load | 2240.29 | 15.13 | 18.07 | 82.75 | 154 | 0.27202 | 0.36254 | 0.36146 | 0.33348 | 0.4223 | 0.083618 | 0.048788 | 0.050905 | 0.11741 | 0.027499 | [10 empty] | 100
Water-Cooled Chiller+WSE | Parameter Unit/MW IT Load | 2907.27 | 22.19 | 26 | 86.25 | 144 | 0.353 | 0.53171 | 0.52008 | 0.34759 | 0.39488 | 0.10851 | 0.071554 | 0.073244 | 0.12238 | 0.025713 | [10 empty] | 100
Water-Cooled Chiller+WSE+ASE | Parameter Unit/MW IT Load | 2240.29 | 15.13 | 18.1 | 81.5 | 163 | 0.27202 | 0.36254 | 0.36206 | 0.32844 | 0.44698 | 0.083618 | 0.048788 | 0.050989 | 0.11564 | 0.029106 | [10 empty] | 100
Evaporative Cooling +ASE | Parameter Unit/MW IT Load | 435.91 | 14.545 | 15.116 | 58.75 | 41 | 0.052928 | 0.34852 | 0.30237 | 0.23676 | 0.11243 | 0.01627 | 0.046902 | 0.042583 | 0.083359 | 0.0073211 | [10 empty] | 50
| Σparameters' weight | 100
Parameter Weight Percentage calculation based on entered paramters' importance comparison by user
Cooling System | Distanc from Ideal Best (S+) | Distanc from Ideal Worst (S-) | S++S- | Perfomance Score (PS) | Rank of Cooling Systems |  |  |  | Parameters
Air-Cooled Chiller | 0.1238 | 0.10389 | 0.22769 | 0.45629 | 4 |  |  | Parameters |  | Energy Usage | Onsite water Use | Total Water Use | Reliability | Maintenance
Air-Cooled Chiller+ ASE | 0.091738 | 0.10451 | 0.19625 | 0.53255 | 2 |  |  |  | Energy Usage | 1 | 3 | 2 | 0.8 | 5
Pre-Cooled-Air-Cooled Chiller | 0.11556 | 0.08174 | 0.1973 | 0.41429 | 7 |  |  |  | Onsite water Use | 0.33333 | 1 | 1 | 0.5 | 2
Pre-Cooled-Air-Cooled Chiller +ASE | 0.085595 | 0.087338 | 0.17293 | 0.50504 | 3 |  |  |  | Total Water Use | 0.5 | 1 | 1 | 0.4 | 1.5
Water-Cooled Chiller | 0.13391 | 0.05194 | 0.18585 | 0.27947 | 8 |  |  |  | Reliability | 1.25 | 2 | 2.5 | 1 | 6
Water-Cooled Chiller+ASE | 0.094095 | 0.073303 | 0.1674 | 0.4379 | 5 |  |  |  | Maintenance | 0.2 | 0.5 | 0.66667 | 0.16667 | 1
Water-Cooled Chiller+WSE | 0.1328 | 0.050167 | 0.18297 | 0.27418 | 9
Water-Cooled Chiller+WSE+ASE | 0.094669 | 0.072452 | 0.16712 | 0.43353 | 6 |  |  |  |  | 0.30457 | 0.13333 | 0.13953 | 0.34884 | 0.064516
Evaporative Cooling +ASE | 0.070206 | 0.13166 | 0.20187 | 0.65222 | 1 |  |  |  | Σparameters' weight | 30.74 | 13.4573 | 14.0832 | 35.208 | 6.5116
100
List of Ranked Cooling Systems | Cooling Eneregy Use (MWh) | Onsite Water Use (acre-ft) | Total Cooling Water (acre-ft) | PUE | Onsite WUE (gal/kWh) | Source WUE (gal/kWh) | Cooling System Availbility (% of the Year)
Evaporative Cooling +ASE | 4359.1 | 145.5027 | 151.217 | 1.1959 | 0.54104 | 1.0517 | 50
Air-Cooled Chiller+ ASE | 28667.6577 | 7.8232 | 45.4033 | 1.4791 | 0.02909 | 0.66065 | 100
Pre-Cooled-Air-Cooled Chiller +ASE | 25600.72 | 68.7649 | 102.3247 | 1.4433 | 0.2557 | 0.872 | 100
Air-Cooled Chiller | 37470.4 | 0.030011 | 49.1496 | 1.5816 | 0.00011159 | 0.67545 | 100
Water-Cooled Chiller+ASE | 22402.9 | 151.3549 | 180.7226 | 1.4061 | 0.5628 | 1.1632 | 100
Water-Cooled Chiller+WSE+ASE | 22402.9 | 151.3549 | 180.7226 | 1.4061 | 0.5628 | 1.1632 | 100
Pre-Cooled-Air-Cooled Chiller | 34408.7 | 59.7016 | 104.8077 | 1.5459 | 0.222 | 0.88211 | 100
Water-Cooled Chiller | 29473.5 | 222.8808 | 261.5173 | 1.4884 | 0.82876 | 1.4643 | 100
Water-Cooled Chiller+WSE | 29072.7 | 221.9805 | 260.0916 | 1.4838 | 0.82541 | 1.459 | 100
IT Load (MW) | 10
Cooling System | Annual Cooling Energy Use (MWh) | Annual IT Energy Use at UPS Outlet (MWh) | Annual IT Energy Use at UPS Inlet (MWh) | Annual Lighting Energy Use (MWh) | Annual Total Energy Use (MWh) | Total Onsite Water Use (kgal) | Total Cooling Water Use (kgal) | Total Source Water Use (kgal) | PUE | WUEOnsite (gal/kWh) | WUESource (gal/kWh) | Cooling System Availbility (% of the Year)
Air-Cooled Chiller | 37470.4 | 87600 | 97333.3333 | 973.3333 | 138548.0272 | 9.7755 | 16009.6363 | 59169.7831 | 1.5816 | 0.00011159 | 0.67545 | 100
Air-Cooled Chiller+ ASE | 28667.6577 | 87600 | 97333.3333 | 973.3333 | 129565.6372 | 2548.2711 | 14789.361 | 57872.7982 | 1.4791 | 0.02909 | 0.66065 | 100
Pre-Cooled-Air-Cooled Chiller | 34408.7 | 87600 | 97333.3333 | 973.3333 | 135423.8435 | 19446.7877 | 34139.3026 | 77272.7689 | 1.5459 | 0.222 | 0.88211 | 100
Pre-Cooled-Air-Cooled Chiller +ASE | 25600.72 | 87600 | 97333.3333 | 973.3333 | 126436.1088 | 22398.9977 | 33330.5052 | 76387.2162 | 1.4433 | 0.2557 | 0.872 | 100
Water-Cooled Chiller | 29473.5 | 87600 | 97333.3333 | 973.3333 | 130387.9252 | 72599.6028 | 85184.7873 | 128275.2468 | 1.4884 | 0.82876 | 1.4643 | 100
Water-Cooled Chiller+ASE | 22402.9 | 87600 | 97333.3333 | 973.3333 | 123173.0272 | 49301.2563 | 58867.2946 | 101896.1389 | 1.4061 | 0.5628 | 1.1632 | 100
Water-Cooled Chiller+WSE | 29072.7 | 87600 | 97333.3333 | 973.3333 | 129978.9456 | 72306.3369 | 84720.3798 | 127807.3467 | 1.4838 | 0.82541 | 1.459 | 100
Water-Cooled Chiller+WSE+ASE | 22402.9 | 87600 | 97333.3333 | 973.3333 | 123173.0272 | 49301.2563 | 58867.2946 | 101896.1389 | 1.4061 | 0.5628 | 1.1632 | 100
Evaporative Cooling +ASE | 4359.1 | 87600 | 97333.3333 | 973.3333 | 104760.9864 | 47395.0279 | 49256.3636 | 92127.9691 | 1.1959 | 0.54104 | 1.0517 | 50
#N/A

## CAC Airflow
Airflow Type
Configuration
0
0
0
|  | Parameters Weight Percentage |  |  |  | 0 | Normalized Performance Values (NPVs) |  |  |  |  | Weighted Normalized Values(WNVs) |  |  |  |  | Ideal Best Value (V-) |  |  |  |  | Ideal Worst Value (V-) |  |  |  |  | Cooling System Availbility (% of the Year)
|  | 30.74 | 13.4573 | 14.0832 | 35.208 | 6.5116
Cooling System | Paramter Unit | Energy Use (MWh) | Onsite Water Use (acre-ft) | Total Cooling Water Use (acre-ft) | Reliability | Maintenance | NPV_Energy | NPV_Onsite Water | NPV_Source Water | NPV_Reliability | NPV_Maintenance | WNV_Energy | WNV_Onsite Water | WNV_Source Water | WNV_Reliability | WNV_Maintenance | V+_Energy | V+_Onsite Water | V+_Source Water | V+_Reliability | V+_Maintenance | V-_Energy | V-_Onsite Water | V-_Source Water | V-_Reliability | V-_Maintenance
Air-Cooled Chiller | Parameter Unit/MW IT Load | 3372.82 | 0.0043 | 4.42 | 89 | 81 | 0.5763 | 0.00013449 | 0.11957 | 0.35403 | 0.22212 | 0.17715 | 1.8099e-05 | 0.016839 | 0.12465 | 0.014464 | 0.036381 | 1.8099e-05 | 0.015914 | 0.12465 | 0.0073211 | 0.17715 | 0.081739 | 0.081224 | 0.099787 | 0.029106 | 100
Air-Cooled Chiller+ ASE | Parameter Unit/MW IT Load | 1940 | 1.8584 | 4.4 | 83.25 | 100 | 0.33148 | 0.058124 | 0.11903 | 0.33116 | 0.27422 | 0.1019 | 0.0078219 | 0.016763 | 0.11659 | 0.017856 | [10 empty] | 100
Pre-Cooled-Air-Cooled Chiller | Parameter Unit/MW IT Load | 3146.89 | 5.268 | 9.39 | 88 | 103 | 0.5377 | 0.16477 | 0.25402 | 0.35005 | 0.28245 | 0.16529 | 0.022173 | 0.035773 | 0.12325 | 0.018392 | [10 empty] | 100
Pre-Cooled-Air-Cooled Chiller +ASE | Parameter Unit/MW IT Load | 1744.252 | 6.089 | 8.375 | 82.25 | 122 | 0.29803 | 0.19044 | 0.22656 | 0.32718 | 0.33455 | 0.091615 | 0.025629 | 0.031907 | 0.11519 | 0.021785 | [10 empty] | 100
Water-Cooled Chiller | Parameter Unit/MW IT Load | 1452.67 | 19.42 | 21.32 | 88.5 | 135 | 0.24821 | 0.60739 | 0.57674 | 0.35204 | 0.3702 | 0.0763 | 0.081739 | 0.081224 | 0.12395 | 0.024106 | [10 empty] | 100
Water-Cooled Chiller+ASE | Parameter Unit/MW IT Load | 1018.31 | 9.84 | 11.18 | 82.75 | 154 | 0.17399 | 0.30776 | 0.30244 | 0.32917 | 0.4223 | 0.053486 | 0.041417 | 0.042593 | 0.11589 | 0.027499 | [10 empty] | 100
Water-Cooled Chiller+WSE | Parameter Unit/MW IT Load | 1407.98 | 19.3 | 21.15 | 86.25 | 144 | 0.24058 | 0.60364 | 0.57214 | 0.34309 | 0.39488 | 0.073953 | 0.081234 | 0.080576 | 0.12079 | 0.025713 | [10 empty] | 100
Water-Cooled Chiller+WSE+ASE | Parameter Unit/MW IT Load | 1018.31 | 9.84 | 11.18 | 81.5 | 163 | 0.17399 | 0.30776 | 0.30244 | 0.32419 | 0.44698 | 0.053486 | 0.041417 | 0.042593 | 0.11414 | 0.029106 | [10 empty] | 100
Evaporative Cooling | Parameter Unit/MW IT Load | 692.6527 | 3.2694 | 4.1771 | 71.25 | 41 | 0.11835 | 0.10226 | 0.113 | 0.28342 | 0.11243 | 0.036381 | 0.013761 | 0.015914 | 0.099787 | 0.0073211 | [10 empty] | 75
| Σparameters' weight | 100
Parameter Weight Percentage calculation based on entered paramters' importance comparison by user
Cooling System | Distanc from Ideal Best (S+) | Distanc from Ideal Worst (S-) | S++S- | Perfomance Score (PS) | Rank of Cooling Systems |  |  |  | Parameters
Air-Cooled Chiller | 0.14096 | 0.10796 | 0.24892 | 0.43372 | 8 |  |  | Parameters |  | Energy Usage | Onsite water Use | Total Water Use | Reliability | Maintenance
Air-Cooled Chiller+ ASE | 0.067304 | 0.12527 | 0.19257 | 0.6505 | 4 |  |  |  | Energy Usage | 1 | 3 | 2 | 0.8 | 5
Pre-Cooled-Air-Cooled Chiller | 0.13277 | 0.080123 | 0.21289 | 0.37636 | 9 |  |  |  | Onsite water Use | 0.33333 | 1 | 1 | 0.5 | 2
Pre-Cooled-Air-Cooled Chiller +ASE | 0.065277 | 0.11484 | 0.18012 | 0.63759 | 5 |  |  |  | Total Water Use | 0.5 | 1 | 1 | 0.4 | 1.5
Water-Cooled Chiller | 0.11322 | 0.10383 | 0.21705 | 0.47836 | 7 |  |  |  | Reliability | 1.25 | 2 | 2.5 | 1 | 6
Water-Cooled Chiller+ASE | 0.056586 | 0.13665 | 0.19324 | 0.70717 | 2 |  |  |  | Maintenance | 0.2 | 0.5 | 0.66667 | 0.16667 | 1
Water-Cooled Chiller+WSE | 0.11199 | 0.10538 | 0.21737 | 0.48478 | 6
Water-Cooled Chiller+WSE+ASE | 0.057473 | 0.13645 | 0.19392 | 0.70363 | 3 |  |  |  |  | 0.30457 | 0.13333 | 0.13953 | 0.34884 | 0.064516
Evaporative Cooling +ASE | 0.028405 | 0.17082 | 0.19922 | 0.85742 | 1 |  |  |  | Σparameters' weight | 30.74 | 13.4573 | 14.0832 | 35.208 | 6.5116
100
List of Ranked Cooling Systems | Cooling Eneregy Use (MWh) | Onsite Water Use (acre-ft) | Total Cooling Water (acre-ft) | PUE | Onsite WUE (gal/kWh) | Source WUE (gal/kWh) | Cooling System Availbility (% of the Year)
Evaporative Cooling +ASE | 69265.2709 | 327.0622 | 417.8614 | 1.2258 | 0.12162 | 0.64504 | 75
Water-Cooled Chiller+ASE | 101831 | 984.3568 | 1117.846 | 1.2637 | 0.36602 | 0.90564 | 100
Water-Cooled Chiller+WSE+ASE | 101831 | 984.3568 | 1117.846 | 1.2637 | 0.36602 | 0.90564 | 100
Air-Cooled Chiller+ ASE | 194000 | 185.904 | 440.2167 | 1.3711 | 0.069127 | 0.65459 | 100
Pre-Cooled-Air-Cooled Chiller +ASE | 174425.2 | 609.1208 | 837.773 | 1.3483 | 0.2265 | 0.80222 | 100
Water-Cooled Chiller+WSE | 140798 | 1930.6998 | 2115.2705 | 1.3091 | 0.71791 | 1.2769 | 100
Water-Cooled Chiller | 145267 | 1942.7041 | 2133.1332 | 1.3143 | 0.72238 | 1.2836 | 100
Air-Cooled Chiller | 337282 | 0.43016 | 442.5698 | 1.538 | 0.00015995 | 0.65689 | 100
Pre-Cooled-Air-Cooled Chiller | 314689 | 526.991 | 939.5137 | 1.5117 | 0.19596 | 0.84145 | 100
IT Load (MW) | 100
Cooling System | Annual Cooling Energy Use (MWh) | Annual IT Energy Use at UPS Outlet (MWh) | Annual IT Energy Use at UPS Inlet (MWh) | Annual Lighting Energy Use (MWh) | Annual Total Energy Use (MWh) | Total Onsite Water Use (kgal) | Total Cooling Water Use (kgal) | Total Source Water Use (kgal) | PUE | WUEOnsite (gal/kWh) | WUESource (gal/kWh) | Cooling System Availbility (% of the Year)
Air-Cooled Chiller | 337282 | 876000 | 973333.3333 | 9733.3333 | 1347294.5578 | 140.1159 | 144159.5299 | 575434.8921 | 1.538 | 0.00015995 | 0.65689 | 100
Air-Cooled Chiller+ ASE | 194000 | 876000 | 973333.3333 | 9733.3333 | 1201088.4354 | 60555.0643 | 143393.0643 | 573419.8262 | 1.3711 | 0.069127 | 0.65459 | 100
Pre-Cooled-Air-Cooled Chiller | 314689 | 876000 | 973333.3333 | 9733.3333 | 1324240.4762 | 171658.3068 | 306030.5098 | 737108.9901 | 1.5117 | 0.19596 | 0.84145 | 100
Pre-Cooled-Air-Cooled Chiller +ASE | 174425.2 | 876000 | 973333.3333 | 9733.3333 | 1181114.1497 | 198410.6739 | 272890.2343 | 702746.4158 | 1.3483 | 0.2265 | 0.80222 | 100
Water-Cooled Chiller | 145267 | 876000 | 973333.3333 | 9733.3333 | 1151360.8844 | 632802.642 | 694831.651 | 1124433.7396 | 1.3143 | 0.72238 | 1.2836 | 100
Water-Cooled Chiller+ASE | 101831 | 876000 | 973333.3333 | 9733.3333 | 1107038.4354 | 320637.384 | 364119.221 | 793342.7959 | 1.2637 | 0.36602 | 0.90564 | 100
Water-Cooled Chiller+WSE | 140798 | 876000 | 973333.3333 | 9733.3333 | 1146800.6803 | 628892.43 | 689013.176 | 1118576.3205 | 1.3091 | 0.71791 | 1.2769 | 100
Water-Cooled Chiller+WSE+ASE | 101831 | 876000 | 973333.3333 | 9733.3333 | 1107038.4354 | 320637.384 | 364119.221 | 793342.7959 | 1.2637 | 0.36602 | 0.90564 | 100
Evaporative Cooling +ASE | 69265.2709 | 876000 | 973333.3333 | 9733.3333 | 1073808.0996 | 106534.9301 | 136111.2007 | 565050.9886 | 1.2258 | 0.12162 | 0.64504 | 75
#N/A

## HAC-VED Airflow
Airflow Type
Configuration
|  | Parameters Weight Percentage |  |  |  |  | Normalized Performance Values (NPVs) |  |  |  |  | Weighted Normalized Values(WNVs) |  |  |  |  | Ideal Best Value (V-) |  |  |  |  | Ideal Worst Value (V-) |  |  |  |  | Cooling System Availbility (% of the Year)
|  | 30.74 | 13.4573 | 14.0832 | 35.208 | 6.5116
Cooling System | Paramter Unit | Energy Use (MWh) | Onsite Water Use (acre-ft) | Total Cooling Water Use (acre-ft) | Reliability | Maintenance | NPV_Energy | NPV_Onsite Water | NPV_Source Water | NPV_Reliability | NPV_Maintenance | WNV_Energy | WNV_Onsite Water | WNV_Source Water | WNV_Reliability | WNV_Maintenance | V+_Energy | V+_Onsite Water | V+_Source Water | V+_Reliability | V+_Maintenance | V-_Energy | V-_Onsite Water | V-_Source Water | V-_Reliability | V-_Maintenance
Air-Cooled Chiller | Parameter Unit/MW IT Load | 3079.35 | 0.007 | 4.04 | 89 | 81 | 0.60091 | 0.00022894 | 0.10076 | 0.34961 | 0.22212 | 0.18472 | 3.0809e-05 | 0.01419 | 0.12309 | 0.014464 | 0.041872 | 3.0809e-05 | 0.01419 | 0.12309 | 0.0073211 | 0.18472 | 0.084988 | 0.074252 | 0.11272 | 0.029106 | 100
Air-Cooled Chiller+ ASE | Parameter Unit/MW IT Load | 1328.13 | 3.0627 | 4.803 | 83.25 | 100 | 0.25918 | 0.10017 | 0.11979 | 0.32702 | 0.27422 | 0.07967 | 0.01348 | 0.01687 | 0.11514 | 0.017856 | [10 empty] | 100
Pre-Cooled-Air-Cooled Chiller | Parameter Unit/MW IT Load | 2908.0108 | 5.271 | 9.081 | 88 | 103 | 0.56748 | 0.17239 | 0.22648 | 0.34568 | 0.28245 | 0.17444 | 0.023199 | 0.031896 | 0.12171 | 0.018392 | [10 empty] | 100
Pre-Cooled-Air-Cooled Chiller +ASE | Parameter Unit/MW IT Load | 1223.2283 | 5.554 | 7.157 | 82.25 | 122 | 0.2387 | 0.18164 | 0.1785 | 0.3231 | 0.33455 | 0.073378 | 0.024444 | 0.025138 | 0.11376 | 0.021785 | [10 empty] | 100
Water-Cooled Chiller | Parameter Unit/MW IT Load | 1398.77 | 19.31 | 21.14 | 88.5 | 135 | 0.27296 | 0.63154 | 0.52724 | 0.34765 | 0.3702 | 0.083908 | 0.084988 | 0.074252 | 0.1224 | 0.024106 | [10 empty] | 100
Water-Cooled Chiller+ASE | Parameter Unit/MW IT Load | 864.1 | 7.46 | 8.59 | 82.75 | 154 | 0.16862 | 0.24398 | 0.21424 | 0.32506 | 0.4223 | 0.051835 | 0.032833 | 0.030172 | 0.11445 | 0.027499 | [10 empty] | 100
Water-Cooled Chiller+WSE | Parameter Unit/MW IT Load | 1268.97 | 19.03 | 20.69 | 86.25 | 144 | 0.24763 | 0.62238 | 0.51602 | 0.33881 | 0.39488 | 0.076122 | 0.083755 | 0.072672 | 0.11929 | 0.025713 | [10 empty] | 100
Water-Cooled Chiller+WSE+ASE | Parameter Unit/MW IT Load | 864.089 | 7.46 | 8.59 | 81.5 | 163 | 0.16862 | 0.24398 | 0.21424 | 0.32015 | 0.44698 | 0.051834 | 0.032833 | 0.030172 | 0.11272 | 0.029106 | [10 empty] | 100
Evaporative Cooling +ASE | Parameter Unit/MW IT Load | 698.014 | 4.5354 | 20.2986 | 81.75 | 41 | 0.13621 | 0.14833 | 0.50625 | 0.32113 | 0.11243 | 0.041872 | 0.019961 | 0.071297 | 0.11306 | 0.0073211 | [10 empty] | 96
| Σparameters' weight | 100
Parameter Weight Percentage calculation based on entered paramters' importance comparison by user
Cooling System | Distanc from Ideal Best (S+) | Distanc from Ideal Worst (S-) | S++S- | Perfomance Score (PS) | Rank of Cooling Systems |  |  |  | Parameters
Air-Cooled Chiller | 0.14303 | 0.10558 | 0.24861 | 0.42469 | 8 |  |  | Parameters |  | Energy Usage | Onsite water Use | Total Water Use | Reliability | Maintenance
Air-Cooled Chiller+ ASE | 0.042321 | 0.13991 | 0.18223 | 0.76776 | 3 |  |  |  | Energy Usage | 1 | 3 | 2 | 0.8 | 5
Pre-Cooled-Air-Cooled Chiller | 0.1362 | 0.076897 | 0.21309 | 0.36086 | 9 |  |  |  | Onsite water Use | 0.33333 | 1 | 1 | 0.5 | 2
Pre-Cooled-Air-Cooled Chiller +ASE | 0.044776 | 0.13612 | 0.1809 | 0.75248 | 4 |  |  |  | Total Water Use | 0.5 | 1 | 1 | 0.4 | 1.5
Water-Cooled Chiller | 0.11347 | 0.1014 | 0.21487 | 0.47192 | 7 |  |  |  | Reliability | 1.25 | 2 | 2.5 | 1 | 6
Water-Cooled Chiller+ASE | 0.043732 | 0.14942 | 0.19316 | 0.77359 | 1 |  |  |  | Maintenance | 0.2 | 0.5 | 0.66667 | 0.16667 | 1
Water-Cooled Chiller+WSE | 0.10934 | 0.10887 | 0.21821 | 0.49892 | 6
Water-Cooled Chiller+WSE+ASE | 0.044864 | 0.14941 | 0.19427 | 0.76906 | 2 |  |  |  |  | 0.30457 | 0.13333 | 0.13953 | 0.34884 | 0.064516
Evaporative Cooling +ASE | 0.06131 | 0.15849 | 0.2198 | 0.72106 | 5 |  |  |  | Σparameters' weight | 30.74 | 13.4573 | 14.0832 | 35.208 | 6.5116
100
List of Ranked Cooling Systems | Cooling Eneregy Use (MWh) | Onsite Water Use (acre-ft) | Total Cooling Water (acre-ft) | PUE | Onsite WUE (gal/kWh) | Source WUE (gal/kWh) | Cooling System Availbility (% of the Year)
Water-Cooled Chiller+ASE | 86410 | 746.2705 | 859.5445 | 1.2458 | 0.27749 | 0.80944 | 100
Water-Cooled Chiller+WSE+ASE | 86408.9 | 746.2705 | 859.543 | 1.2458 | 0.27749 | 0.80944 | 100
Air-Cooled Chiller+ ASE | 132813 | 306.3838 | 480.487 | 1.2998 | 0.11393 | 0.66895 | 100
Pre-Cooled-Air-Cooled Chiller +ASE | 122322.8312 | 555.6014 | 715.9531 | 1.2876 | 0.2066 | 0.75641 | 100
Evaporative Cooling +ASE | 69801.3987 | 453.7022 | 545.2042 | 1.2264 | 0.16871 | 0.69239 | 96
Water-Cooled Chiller+WSE | 126897 | 1903.69 | 2070.038 | 1.2929 | 0.70787 | 1.26 | 100
Water-Cooled Chiller | 139877 | 1931.7001 | 2115.0635 | 1.3081 | 0.71829 | 1.2768 | 100
Air-Cooled Chiller | 307935 | 0.70025 | 404.3692 | 1.5038 | 0.00026038 | 0.64239 | 100
Pre-Cooled-Air-Cooled Chiller | 290801.0827 | 527.2911 | 908.4993 | 1.4839 | 0.19607 | 0.82968 | 100
IT Load (MW) | 100
Cooling System | Annual Cooling Energy Use (MWh) | Annual IT Energy Use at UPS Outlet (MWh) | Annual IT Energy Use at UPS Inlet (MWh) | Annual Lighting Energy Use (MWh) | Annual Total Energy Use (MWh) | Total Onsite Water Use (kgal) | Total Cooling Water Use (kgal) | Total Source Water Use (kgal) | PUE | WUEOnsite (gal/kWh) | WUESource (gal/kWh) | Cooling System Availbility (% of the Year)
Air-Cooled Chiller | 307935 | 876000 | 973333.3333 | 9733.3333 | 1317348.6395 | 228.0957 | 131716.3407 | 562735.9647 | 1.5038 | 0.00026038 | 0.64239 | 100
Air-Cooled Chiller+ ASE | 132813 | 876000 | 973333.3333 | 9733.3333 | 1138652.7211 | 99799.2831 | 156510.4341 | 586003.995 | 1.2998 | 0.11393 | 0.66895 | 100
Pre-Cooled-Air-Cooled Chiller | 290801.0827 | 876000 | 973333.3333 | 9733.3333 | 1299865.0504 | 171756.0621 | 295928.1244 | 726798.4386 | 1.4839 | 0.19607 | 0.82968 | 100
Pre-Cooled-Air-Cooled Chiller +ASE | 122322.8312 | 876000 | 973333.3333 | 9733.3333 | 1127948.4672 | 180977.6454 | 233209.4943 | 662611.6409 | 1.2876 | 0.2066 | 0.75641 | 100
Water-Cooled Chiller | 139877 | 876000 | 973333.3333 | 9733.3333 | 1145860.8844 | 629218.281 | 688945.76 | 1118500.8786 | 1.3081 | 0.71829 | 1.2768 | 100
Water-Cooled Chiller+ASE | 86410 | 876000 | 973333.3333 | 9733.3333 | 1091302.7211 | 243084.846 | 279981.916 | 709071.1079 | 1.2458 | 0.27749 | 0.80944 | 100
Water-Cooled Chiller+WSE | 126897 | 876000 | 973333.3333 | 9733.3333 | 1132615.9864 | 620094.453 | 674279.472 | 1103721.4792 | 1.2929 | 0.70787 | 1.26 | 100
Water-Cooled Chiller+WSE+ASE | 86408.9 | 876000 | 973333.3333 | 9733.3333 | 1091301.5986 | 243084.846 | 279981.4463 | 709070.6286 | 1.2458 | 0.27749 | 0.80944 | 100
Evaporative Cooling +ASE | 69801.3987 | 876000 | 973333.3333 | 9733.3333 | 1074355.1687 | 147785.7491 | 177590.9463 | 606535.4061 | 1.2264 | 0.16871 | 0.69239 | 96
#N/A

## CAC and HAC-VED Airflow
Airflow Type
Configuration
|  | Parameters Weight Percentage |  |  |  |  | Normalized Performance Values (NPVs) |  |  |  |  | Weighted Normalized Values(WNVs) |  |  |  |  | Ideal Best Value (V-) |  |  |  |  | Ideal Worst Value (V-) |  |  |  |  | Cooling System Availbility (% of the Year)
|  | 20 | 30 | 10 | 30 | 10
Cooling System | Paramter Unit | Energy Use (MWh) | Onsite Water Use (acre-ft) | Total Cooling Water Use (acre-ft) | Reliability | Maintenance | NPV_Energy | NPV_Onsite Water | NPV_Source Water | NPV_Reliability | NPV_Maintenance | WNV_Energy | WNV_Onsite Water | WNV_Source Water | WNV_Reliability | WNV_Maintenance | V+_Energy | V+_Onsite Water | V+_Source Water | V+_Reliability | V+_Maintenance | V-_Energy | V-_Onsite Water | V-_Source Water | V-_Reliability | V-_Maintenance
Air-Cooled Chiller | Parameter Unit/MW IT Load | 2963.5919 | 0.0062 | 3.89 | 89 | 81 | 0.61731 | 0.0001818 | 0.1026 | 0.34917 | 0.22212 | 0.12346 | 5.454e-05 | 0.01026 | 0.10475 | 0.022212 | 0.025206 | 5.454e-05 | 0.01026 | 0.10475 | 0.011243 | 0.12346 | 0.16714 | 0.054175 | 0.095923 | 0.044698 | 100
Air-Cooled Chiller+ ASE | Parameter Unit/MW IT Load | 1164.8134 | 3.079 | 4.605 | 83.25 | 100 | 0.24263 | 0.090284 | 0.12146 | 0.32661 | 0.27422 | 0.048526 | 0.027085 | 0.012146 | 0.097983 | 0.027422 | [10 empty] | 100
Pre-Cooled-Air-Cooled Chiller | Parameter Unit/MW IT Load | 2798.2163 | 5.27 | 8.937 | 88 | 103 | 0.58286 | 0.15453 | 0.23572 | 0.34525 | 0.28245 | 0.11657 | 0.046359 | 0.023572 | 0.10357 | 0.028245 | [10 empty] | 100
Pre-Cooled-Air-Cooled Chiller +ASE | Parameter Unit/MW IT Load | 1074.7174 | 5.238 | 6.65 | 82.25 | 122 | 0.22386 | 0.15359 | 0.1754 | 0.32269 | 0.33455 | 0.044772 | 0.046077 | 0.01754 | 0.096806 | 0.033455 | [10 empty] | 100
Water-Cooled Chiller | Parameter Unit/MW IT Load | 1173.66 | 19 | 20.54 | 88.5 | 135 | 0.24447 | 0.55713 | 0.54175 | 0.34721 | 0.3702 | 0.048894 | 0.16714 | 0.054175 | 0.10416 | 0.03702 | [10 empty] | 100
Water-Cooled Chiller+ASE | Parameter Unit/MW IT Load | 764.07 | 6.94 | 7.94 | 82.75 | 154 | 0.15915 | 0.2035 | 0.20942 | 0.32465 | 0.4223 | 0.031831 | 0.06105 | 0.020942 | 0.097395 | 0.04223 | [10 empty] | 100
Water-Cooled Chiller+WSE | Parameter Unit/MW IT Load | 1173.66 | 19 | 20.54 | 86.25 | 144 | 0.24447 | 0.55713 | 0.54175 | 0.33838 | 0.39488 | 0.048894 | 0.16714 | 0.054175 | 0.10151 | 0.039488 | [10 empty] | 100
Water-Cooled Chiller+WSE+ASE | Parameter Unit/MW IT Load | 764.071 | 6.94 | 7.94 | 81.5 | 163 | 0.15915 | 0.2035 | 0.20942 | 0.31974 | 0.44698 | 0.031831 | 0.06105 | 0.020942 | 0.095923 | 0.044698 | [10 empty] | 100
Evaporative Cooling +ASE | Parameter Unit/MW IT Load | 605.057 | 16.734 | 17.526 | 82.75 | 41 | 0.12603 | 0.49068 | 0.46226 | 0.32465 | 0.11243 | 0.025206 | 0.14721 | 0.046226 | 0.097395 | 0.011243 | [10 empty] | 98
| Σparameters' weight | 100
Parameter Weight Percentage calculation based on entered paramters' importance comparison by user
Cooling System | Distanc from Ideal Best (S+) | Distanc from Ideal Worst (S-) | S++S- | Perfomance Score (PS) | Rank of Cooling Systems |  |  |  | Parameters
Air-Cooled Chiller | 0.098866 | 0.17444 | 0.27331 | 0.63826 | 5 |  |  | Parameters |  | Energy Usage | Onsite water Use | Total Water Use | Reliability | Maintenance
Air-Cooled Chiller+ ASE | 0.039819 | 0.16523 | 0.20505 | 0.8058 | 1 |  |  |  | Energy Usage | 1 | 3 | 2 | 0.8 | 5
Pre-Cooled-Air-Cooled Chiller | 0.10469 | 0.1261 | 0.23079 | 0.54639 | 6 |  |  |  | Onsite water Use | 0.33333 | 1 | 1 | 0.5 | 2
Pre-Cooled-Air-Cooled Chiller +ASE | 0.055771 | 0.14939 | 0.20516 | 0.72816 | 2 |  |  |  | Total Water Use | 0.5 | 1 | 1 | 0.4 | 1.5
Water-Cooled Chiller | 0.17627 | 0.075413 | 0.25168 | 0.29963 | 8 |  |  |  | Reliability | 1.25 | 2 | 2.5 | 1 | 6
Water-Cooled Chiller+ASE | 0.069948 | 0.1441 | 0.21404 | 0.67321 | 3 |  |  |  | Maintenance | 0.2 | 0.5 | 0.66667 | 0.16667 | 1
Water-Cooled Chiller+WSE | 0.17668 | 0.074958 | 0.25164 | 0.29788 | 9
Water-Cooled Chiller+WSE+ASE | 0.071243 | 0.14407 | 0.21531 | 0.66912 | 4 |  |  |  |  | 0.30457 | 0.13333 | 0.13953 | 0.34884 | 0.064516
Evaporative Cooling +ASE | 0.15166 | 0.106 | 0.25766 | 0.4114 | 7 |  |  |  | Σparameters' weight | 30.74 | 13.4573 | 14.0832 | 35.208 | 6.5116
100
List of Ranked Cooling Systems | Cooling Eneregy Use (MWh) | Onsite Water Use (acre-ft) | Total Cooling Water (acre-ft) | PUE | Onsite WUE (gal/kWh) | Source WUE (gal/kWh) | Cooling System Availbility (% of the Year)
Air-Cooled Chiller+ ASE | 23296.2676 | 61.602 | 90.2099 | 1.885 | 0.11453 | 0.86852 | 100
Pre-Cooled-Air-Cooled Chiller +ASE | 21494.3476 | 104.798 | 131.193 | 1.8721 | 0.19484 | 0.94368 | 100
Water-Cooled Chiller+ASE | 15281.4 | 138.8503 | 157.6159 | 1.8278 | 0.25815 | 0.98926 | 100
Water-Cooled Chiller+WSE+ASE | 15281.42 | 138.8503 | 157.6159 | 1.8278 | 0.25815 | 0.98926 | 100
Air-Cooled Chiller | 59271.838 | 0.12404 | 72.9099 | 2.1416 | 0.00023063 | 0.85689 | 100
Pre-Cooled-Air-Cooled Chiller | 55964.3268 | 105.4382 | 174.1624 | 2.118 | 0.19603 | 1.0432 | 100
Evaporative Cooling +ASE | 12101.14 | 334.8013 | 349.6615 | 1.8051 | 0.62246 | 1.3445 | 98
Water-Cooled Chiller | 23473.2 | 380.1378 | 408.9629 | 1.8862 | 0.70675 | 1.4612 | 100
Water-Cooled Chiller+WSE | 23473.2 | 380.1378 | 408.9629 | 1.8862 | 0.70675 | 1.4612 | 100
IT Load (MW) | 20
Cooling System | Annual Cooling Energy Use (MWh) | Annual IT Energy Use at UPS Outlet (MWh) | Annual IT Energy Use at UPS Inlet (MWh) | Annual Lighting Energy Use (MWh) | Annual Total Energy Use (MWh) | Total Onsite Water Use (kgal) | Total Cooling Water Use (kgal) | Total Source Water Use (kgal) | PUE | WUEOnsite (gal/kWh) | WUESource (gal/kWh) | Cooling System Availbility (% of the Year)
Air-Cooled Chiller | 59271.838 | 175200 | 219000 | 21900 | 375214.7975 | 40.4055 | 23749.1407 | 150126.3245 | 2.1416 | 0.00023063 | 0.85689 | 100
Air-Cooled Chiller+ ASE | 23296.2676 | 175200 | 219000 | 21900 | 330245.3345 | 20065.8095 | 29384.3166 | 152163.9433 | 1.885 | 0.11453 | 0.86852 | 100
Pre-Cooled-Air-Cooled Chiller | 55964.3268 | 175200 | 219000 | 21900 | 371080.4085 | 34344.6954 | 56730.4261 | 182776.8588 | 2.118 | 0.19603 | 1.0432 | 100
Pre-Cooled-Air-Cooled Chiller +ASE | 21494.3476 | 175200 | 219000 | 21900 | 327992.9345 | 34136.1508 | 42733.8898 | 165333.3246 | 1.8721 | 0.19484 | 0.94368 | 100
Water-Cooled Chiller | 23473.2 | 175200 | 219000 | 21900 | 330466.5 | 123823.38 | 133212.66 | 256009.98 | 1.8862 | 0.70675 | 1.4612 | 100
Water-Cooled Chiller+ASE | 15281.4 | 175200 | 219000 | 21900 | 320226.75 | 45228.1188 | 51340.6788 | 173318.8188 | 1.8278 | 0.25815 | 0.98926 | 100
Water-Cooled Chiller+WSE | 23473.2 | 175200 | 219000 | 21900 | 330466.5 | 123823.38 | 133212.66 | 256009.98 | 1.8862 | 0.70675 | 1.4612 | 100
Water-Cooled Chiller+WSE+ASE | 15281.42 | 175200 | 219000 | 21900 | 320226.775 | 45228.1188 | 51340.6868 | 173318.8288 | 1.8278 | 0.25815 | 0.98926 | 100
Evaporative Cooling +ASE | 12101.14 | 175200 | 219000 | 21900 | 316251.425 | 109055.8127 | 113896.2687 | 235556.3827 | 1.8051 | 0.62246 | 1.3445 | 98
#N/A

## Reliability Default Values
Scores range from 1 to 10 (1 as the lowest and 10 as the highest)
Cooling System Type | Annual Availability | Fluctuation of IT Room Air Supply Affected by Outdoor Condition | Lifetime | IT Room Air Contamination | Complexity | Overall Reliability (out of 100)
Air-Cooled Chiller | 50 | 10 | 9 | 10 | 10 | 89
Air-Cooled Chiller + ASE | 50 | 8.5 | 8.75 | 8 | 8 | 83.25
Pre-Cooled-Air-Cooled Chiller | 50 | 10 | 9 | 10 | 9 | 88
Pre-Cooled-Air-Cooled Chiller + ASE | 50 | 8.5 | 8.75 | 8 | 7 | 82.25
Water-Cooled Chiller | 50 | 10 | 10 | 10 | 8.5 | 88.5
Water-Cooled Chiller + ASE | 50 | 8.5 | 9.75 | 8 | 6.5 | 82.75
Water-Cooled Chiller + WSE | 50 | 9 | 9.75 | 10 | 7.5 | 86.25
Water-Cooled Chiller + WSE + ASE | 50 | 8.5 | 9.5 | 8 | 5.5 | 81.5
Evaporative Cooling + ASE (No Airflow Containment) | 25 | 8.5 | 9.25 | 8 | 8 | 58.75
Evaporative Cooling + ASE (CAC Airflow) | 37.5 | 8.5 | 9.25 | 8 | 8 | 71.25
Evaporative Cooling + ASE (HAC-VED Airflow) | 48 | 8.5 | 9.25 | 8 | 8 | 81.75
Evaporative Cooling + ASE (CAC and HAC-VED Airflow) | 49 | 8.5 | 9.25 | 8 | 8 | 82.75
1. Availability: Fraction of the year a cooling system can provide IT room air supply at ASHRAE's recommended condition.
Notes:
i) For all cooling systems but Evaporative Cooling +ASE, the IT room air supply is cooled by chilled water provided by a chilled water plant. ASE and WSE are used when the reccommended IT room air condition (Temperature and humidity) is met using economizer mode.
ii) For the Evaporative Cooling + ASE system, the temperature and/or humidity condition of the reccommended IT room air condition is not met for about 10% of the 8760 hours per year.
2. Complexity: This score evaluates the complexity of the cooling system based on the extent of subsystems and thier hybrids (i.e., cooling towers, pre-evapoartors, and economization). The more complex the system, the lower the score. Air-cooled chiller and evaporative cooling systems are considered the least complex as they do not involve a subsystem or hybrid.
Notes:
i) WSE: -1
ii) ASE: -2
iii) Pre-evaporative cooling effect: -1
iv) Cooling tower: -1.5
3. Fluctuation of IT Room Air Supply Affected by Outdoor Condition: This score is indicative of the affect that the outdoor condition has on the cooling system performance, regardless of energy and water use, and how accurately the IT room air condition can be controlled.
Notes:
i) Outdoor temperature and humidity effect on ASE: -1.5
ii) Evaporative cooling + ASE due to lower control in humid seasons: -1.5
4. Lifetime: longer lifetime the higher reliability
Notes:
i) Air-cooled chillers mean lifetime is 15-20 years1: -3
ii) Water-cooled chillers mean lifetime is about 25-30 years1: baseline
iii) Cooling tower lifetime is 15-20 years2: -1.5
iv) Effect of ASE air filters on lifetime: -0.25
v) Effect of evaporative pads on lifetime: -0.5
iv) Effect of WSE heat exchangers on lifetime: -0.25
1Reference: https://www.johnsoncontrols.com/campaigns/chiller-life-cycle#:~:text=According%20to%20Consulting%2DSpecifying%20Engineer,expectancy%20of%2015%2D20%20years.
2Reference: https://www.bondwater.com/cooling-tower-refurbishing-vs-the-cost-of-tower-replacement/#:~:text=Cooling%20Tower%20Replacement%20can%20be,to%20be%20rebuilt%20or%20replaced.
5. IT Room Air Contamination: How much the IT room supply air is exposed to the contaminations.
Notes:
i) If ASE is used, the IT room is highly exposed to the outdoor contamination. Therefore, the score is the minimum (8).
ii) If the cooling system is not integrated with ASE, the IT room is not exposed to the outdoor contamination. Therefore, the score is the minimum (10).

## Maintenance Default Values
Weights range from 1 to 10 (1 as the lowest and 10 as the highest)
| Annual Maintenance Actions | Semi-Annual Maintenance Actions | Monthly Maintenance Actions | Weekly Maintenance Actions | Daily Maintenance Actions | Water Treatment Requirement | Overall Maintenance Value
| 5 | 4 | 3 | 2 | 1 | 10
Air-Cooled Chiller | 10 | 4 | 0 | 6 | 3 | 0 | 81
Air-Cooled Chiller + ASE | 11 | 7 | 0 | 7 | 3 | 0 | 100
Pre-Cooled-Air-Cooled Chiller | 11 | 4 | 1 | 8 | 3 | 1 | 103
Pre-Cooled-Air-Cooled Chiller + ASE | 12 | 7 | 1 | 9 | 3 | 1 | 122
Water-Cooled Chiller | 13 | 4 | 4 | 13 | 6 | 1 | 135
Water-Cooled Chiller + ASE | 14 | 7 | 4 | 14 | 6 | 1 | 154
Water-Cooled Chiller + WSE | 14 | 4 | 4 | 15 | 6 | 1 | 144
Water-Cooled Chiller + WSE + ASE | 15 | 7 | 4 | 16 | 6 | 1 | 163
Evaporative Cooling + ASE | 2 | 3 | 1 | 3 | 0 | 1 | 41
Note on C4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Score or weight?
Note: For each cooling system the number and frequency of maintenance actions were listed below. A score was also assigned for each action (higher score means more severe action). Then for each cooling system, the overall maintenance score was calculated based on following formula.
Note: The higher maintenance score will negatively affect the rank of cooling system in MCDST.
Note: The maintenance actions for chillers, cooling tower, and air-side economizer are listed with details in the reference tabs; however, for evaporative cooling and water-side economizer there is no such a list of actions. So for pre-cooled air-cooled chiller, water-side economizer, and evaporative cooling systems I listed the actions based on available material and my thoughts. Please see the next sheets and cited references below.
1. Maintenance Actions Weights
Annual Actions: 5
Semi-Annual: 4
Monthly: 3
Weekly: 2
Daily: 1
Water Treatment Requirement: 10
Number of Maintenance Actions for a Chiller1:
Annual Actions: 10
Semi-Annual: 4
Monthly: 0
Weekly: 6
Daily: 3
Water Treatment Requirement: No
1Reference: https://www.energy.gov/sites/prod/files/2013/10/f3/omguide_complete.pdf
Number of Maintenance Actions for a Cooling Tower1:
Annual Actions: 3
Semi-Annual: 0
Monthly: 4
Weekly: 7
Daily: 3
Water Treatment Requirement: Yes
1Reference: https://www.energy.gov/sites/prod/files/2013/10/f3/omguide_complete.pdf
Number of Maintenance Actions for an Air-Side Economizer2:
Annual Actions: 1
Semi-Annual: 3
Monthly: 0
Weekly: 1
Daily: 0
Water Treatment Requirement: No
2Reference: https://www.pnnl.gov/projects/best-practices/air-side-economizers#Maintenance%20Checklist
Number of Pre-cooled Air-Cooled Chillers3,4:
Note: The details of maintenance procedure and the frequency of steps have not been well defined for Pre-cooled Air-Cooled Chillers.
The maintenance procedure can be assumed based on air-cooled chiller maintenance and evaporative cooling maintenance procedures.
1. Replacing/ cleaning cooling pads (Annually)
2. Checking cooling pads (Monthly)
3. Checking fan belts (Weekly)
4. Checking spray systems (Weekly)
5. Checking water quality and treatment: Yes, but not as severe as other systems
3,4References:
https://www.chemaqua.com/en-us/Blogs/how-do-adiabatic-cooling-systems-work
https://www.process-cooling.com/articles/89897-how-to-successfully-implement-evaporative-cooling
Number of Maintenance Actions for a Water-Side Economizer5:
Note: The details of maintenance procedure and the frequency of steps have not been well defined for WSE.
The maintenance procedure can be assumed as follows:
1. Checking heat exchanger for fouling/scaling using their approach temperature (weekly)
2. Cleaning heat exchangers as required (Depending on water quality may need to be down very frequently. In this case since we define a score for water treatment and quality check, the frequency of heat exchanger cleaning may be needed as annually
3. Checking water quality and treatment (Weekly)
Annual Actions: 1
Semi-Annual: 0
Monthly: 0
Weekly: 2
Daily: 0
Water Treatment Requirement: Yes
5Reference: https://www.thefreelibrary.com/Waterside+and+airside+economizers+design+considerations+for+data...-a0227975377
Number of Adiabatic Evaporative Cooling Systems3,4:
Note: The details of maintenance procedure and the frequency of steps have not been well defined for evaporative cooling.
The maintenance procedure can be assumed as follows:
1. Replacing/ cleaning cooling pads (Annually)
2. Checking cooling pads (Monthly)
3. Checking fan belts (Weekly)
4. Checking spray systems (Weekly)
5. Checking water quality and treatment: Yes
3,4References:
https://www.chemaqua.com/en-us/Blogs/how-do-adiabatic-cooling-systems-work
https://www.process-cooling.com/articles/89897-how-to-successfully-implement-evaporative-cooling
Note: For each cooling system the number and frequency of maintenance actions were listed below. A score was also assigned for each action (higher score means more severe action). Then for each cooling system, the overall maintenance score was calculated based on following formula. 𝑂𝑣𝑒𝑟𝑎𝑙𝑙 𝑀𝑎𝑖𝑛𝑡𝑒𝑛𝑎𝑛𝑐𝑒 𝑉𝑎𝑙𝑢𝑒=∑▒(𝑛𝑢𝑚𝑏𝑒𝑟 𝑜𝑓 𝑎𝑐𝑡𝑖𝑜𝑛×𝑎𝑐𝑡𝑖𝑜𝑛 𝑤𝑒𝑖𝑔ℎ𝑡)
Note: The higher maintenance score will negatively affect the rank of cooling system in MCDST.
Note: The maintenance actions for chillers, cooling tower, and air-side economizer are listed with details in the reference tabs; however, for evaporative cooling and water-side economizer there is no such a list of actions. So for pre-cooled air-cooled chiller, water-side economizer, and evaporative cooling systems I listed the actions based on available material and my thoughts. Please see the next sheets and cited references below.
1. Maintenance Actions Weights
Annual Actions: 5
Semi-Annual: 4
Monthly: 3
Weekly: 2
Daily: 1
Water Treatment Requirement: 10
Number of Maintenance Actions for a Chiller1:
Annual Actions: 10
Semi-Annual: 4
Monthly: 0
Weekly: 6
Daily: 3
Water Treatment Requirement: No
1Reference: https://www.energy.gov/sites/prod/files/2013/10/f3/omguide_complete.pdf
Number of Maintenance Actions for a Cooling Tower1:
Annual Actions: 3
Semi-Annual: 0
Monthly: 4
Weekly: 7
Daily: 3
Water Treatment Requirement: Yes
1Reference: https://www.energy.gov/sites/prod/files/2013/10/f3/omguide_complete.pdf
Number of Maintenance Actions for an Air-Side Economizer2:
Annual Actions: 1
Semi-Annual: 3
Monthly: 0
Weekly: 1
Daily: 0
Water Treatment Requirement: No
2Reference: https://www.pnnl.gov/projects/best-practices/air-side-economizers#Maintenance%20Checklist
Number of Pre-cooled Air-Cooled Chillers3,4:
Note: The details of maintenance procedure and the frequency of steps have not been well defined for Pre-cooled Air-Cooled Chillers.
The maintenance procedure can be assumed based on air-cooled chiller maintenance and evaporative cooling maintenance procedures.
1. Replacing/ cleaning cooling pads (Annually)
2. Checking cooling pads (Monthly)
3. Checking fan belts (Weekly)
4. Checking spray systems (Weekly)
5. Checking water quality and treatment: Yes, but not as severe as other systems
3,4References:
https://www.chemaqua.com/en-us/Blogs/how-do-adiabatic-cooling-systems-work
https://www.process-cooling.com/articles/89897-how-to-successfully-implement-evaporative-cooling
Number of Maintenance Actions for a Water-Side Economizer5:
Note: The details of maintenance procedure and the frequency of steps have not been well defined for WSE.
The maintenance procedure can be assumed as follows:
1. Checking heat exchanger for fouling/scaling using their approach temperature (weekly)
2. Cleaning heat exchangers as required (Depending on water quality may need to be down very frequently. In this case since we define a score for water treatment and quality check, the frequency of heat exchanger cleaning may be needed as annually
3. Checking water quality and treatment (Weekly)
Annual Actions: 1
Semi-Annual: 0
Monthly: 0
Weekly: 2
Daily: 0
Water Treatment Requirement: Yes
5Reference: https://www.thefreelibrary.com/Waterside+and+airside+economizers+design+considerations+for+data...-a0227975377
Number of Adiabatic Evaporative Cooling Systems3,4:
Note: The details of maintenance procedure and the frequency of steps have not been well defined for evaporative cooling.
The maintenance procedure can be assumed as follows:
1. Replacing/ cleaning cooling pads (Annually)
2. Checking cooling pads (Monthly)
3. Checking fan belts (Weekly)
4. Checking spray systems (Weekly)
5. Checking water quality and treatment: Yes
3,4References:
https://www.chemaqua.com/en-us/Blogs/how-do-adiabatic-cooling-systems-work
https://www.process-cooling.com/articles/89897-how-to-successfully-implement-evaporative-cooling
Action Score
Action Weight
Action Frequency

## Reliability Customized Values
Scores range from 1 to 10 (1 as the lowest and 10 as the highest)
Cooling System Type | Annual Availability | Fluctuation of IT Room Air Supply Affected by Outdoor Condition | Lifetime | IT Room Air Contamination | Complexity | Overall Reliability (out of 50) | Overall Reliability (Scaled to 100)
Air-Cooled Chiller | [5 empty] | 0 | 0
Air-Cooled Chiller + ASE | [5 empty] | 0 | 0
Pre-Cooled-Air-Cooled Chiller | [5 empty] | 0 | 0
Pre-Cooled-Air-Cooled Chiller + ASE | [5 empty] | 0 | 0
Water-Cooled Chiller | [5 empty] | 0 | 0
Water-Cooled Chiller + ASE | [5 empty] | 0 | 0
Water-Cooled Chiller + WSE | [5 empty] | 0 | 0
Water-Cooled Chiller + WSE + ASE | [5 empty] | 0 | 0
Evaporative Cooling + ASE | [5 empty] | 0 | 0
1. Availability: Fraction of the year a cooling system can provide IT room air supply at ASHRAE's recommended condition.
Notes:
i) For all cooling systems but Evaporative Cooling +ASE, the IT room air supply is cooled by chilled water provided by a chilled water plant. ASE and WSE are used when the reccommended IT room air condition (Temperature and humidity) is met using economizer mode.
ii) For the Evaporative Cooling + ASE system, the temperature and/or humidity condition of the reccommended IT room air condition is not met for about 10% of the 8760 hours per year.
2. Complexity: This score evaluates the complexity of the cooling system based on the extent of subsystems and thier hybrids (i.e., cooling towers, pre-evapoartors, and economization). The more complex the system, the lower the score. Air-cooled chiller and evaporative cooling systems are considered the least complex as they do not involve a subsystem or hybrid.
Notes:
i) WSE: -1
ii) ASE: -2
iii) Pre-evaporative cooling effect: -1
iv) Cooling tower: -1.5
3. Fluctuation of IT Room Air Supply Affected by Outdoor Condition: This score is indicative of the affect that the outdoor condition has on the cooling system performance, regardless of energy and water use, and how accurately the IT room air condition can be controlled.
Notes:
i) Outdoor temperature and humidity effect on ASE: -1.5
ii) Outdoor temperature and humidity effect on WSE: -1
iv) Evaporative cooling + ASE due to lower control in humid seasons: -1.5
4. Lifetime: longer lifetime the higher reliability
Notes:
i) Air-cooled chillers mean lifetime is 15-20 years1: -3
ii) Water-cooled chillers mean lifetime is about 25-30 years1: baseline
iii) Cooling tower lifetime is 15-20 years2: -1.5
iv) Effect of ASE air filters on lifetime: -0.25
v) Effect of evaporative pads on lifetime: -0.5
iv) Effect of WSE heat exchangers on lifetime: -0.25
1Reference: https://www.johnsoncontrols.com/campaigns/chiller-life-cycle#:~:text=According%20to%20Consulting%2DSpecifying%20Engineer,expectancy%20of%2015%2D20%20years.
2Reference: https://www.bondwater.com/cooling-tower-refurbishing-vs-the-cost-of-tower-replacement/#:~:text=Cooling%20Tower%20Replacement%20can%20be,to%20be%20rebuilt%20or%20replaced.
5. IT Room Air Contamination: How much the IT room supply air is exposed to the contaminations.
Notes:
i) If ASE is used, the IT room is highly exposed to the outdoor contamination. Therefore, the score is the minimum (8).
ii) If the cooling system is not integrated with ASE, the IT room is not exposed to the outdoor contamination. Therefore, the score is the minimum (10).

## Maintenance Customized Values
Weights range from 1 to 10 (1 as the lowest and 10 as the highest)
| Annual Maintenance Actions | Semi-Annual Maintenance Actions | Monthly Maintenance Actions | Weekly Maintenance Actions | Daily Maintenance Actions | Water Treatment Requirement | Overall Maintenance Score
| 5 | 4 | 3 | 2 | 1 | 10
Air-Cooled Chiller | [6 empty] | 0
Air-Cooled Chiller + ASE | [6 empty] | 0
Pre-Cooled-Air-Cooled Chiller | [6 empty] | 0
Pre-Cooled-Air-Cooled Chiller + ASE | [6 empty] | 0
Water-Cooled Chiller | [6 empty] | 0
Water-Cooled Chiller + ASE | [6 empty] | 0
Water-Cooled Chiller + WSE | [6 empty] | 0
Water-Cooled Chiller + WSE + ASE | [6 empty] | 0
Evaporative Cooling + ASE | [6 empty] | 0
Note on C4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Score or weight?
Note: For each cooling system the number and frequency of maintenance actions were listed below. A score was also assigned for each action (higher score means more severe action). Then for each cooling system, the overall maintenance score was calculated based on following formula.
Note: The higher maintenance score will negatively affect the rank of cooling system in MCDST.
Note: The maintenance actions for chillers, cooling tower, and air-side economizer are listed with details in the reference tabs; however, for evaporative cooling and water-side economizer there is no such a list of actions. So for pre-cooled air-cooled chiller, water-side economizer, and evaporative cooling systems I listed the actions based on available material and my thoughts. Please see the next sheets and cited references below.
1. Maintenance Actions Scores
Annual Actions: 5
Semi-Annual: 4
Monthly: 3
Weekly: 2
Daily: 1
Water Treatment Requirement: 10
Number of Maintenance Actions for a Chiller1:
Annual Actions: 10
Semi-Annual: 4
Monthly: 0
Weekly: 6
Daily: 3
Water Treatment Requirement: No
1Reference: https://www.energy.gov/sites/prod/files/2013/10/f3/omguide_complete.pdf
Number of Maintenance Actions for a Cooling Tower1:
Annual Actions: 3
Semi-Annual: 0
Monthly: 4
Weekly: 7
Daily: 3
Water Treatment Requirement: Yes
1Reference: https://www.energy.gov/sites/prod/files/2013/10/f3/omguide_complete.pdf
Number of Maintenance Actions for an Air-Side Economizer2:
Annual Actions: 1
Semi-Annual: 3
Monthly: 0
Weekly: 1
Daily: 0
Water Treatment Requirement: No
2Reference: https://www.pnnl.gov/projects/best-practices/air-side-economizers#Maintenance%20Checklist
Number of Pre-cooled Air-Cooled Chillers3,4:
Note: The details of maintenance procedure and the frequency of steps have not been well defined for Pre-cooled Air-Cooled Chillers.
The maintenance procedure can be assumed based on air-cooled chiller maintenance and evaporative cooling maintenance procedures.
1. Replacing/ cleaning cooling pads (Annually)
2. Checking cooling pads (Monthly)
3. Checking fan belts (Weekly)
4. Checking spray systems (Weekly)
5. Checking water quality and treatment: Yes, but not as severe as other systems
3,4References:
https://www.chemaqua.com/en-us/Blogs/how-do-adiabatic-cooling-systems-work
https://www.process-cooling.com/articles/89897-how-to-successfully-implement-evaporative-cooling
Number of Maintenance Actions for a Water-Side Economizer5:
Note: The details of maintenance procedure and the frequency of steps have not been well defined for WSE.
The maintenance procedure can be assumed as follows:
1. Checking heat exchanger for fouling/scaling using their approach temperature (weekly)
2. Cleaning heat exchangers as required (Depending on water quality may need to be down very frequently. In this case since we define a score for water treatment and quality check, the frequency of heat exchanger cleaning may be needed as annually
3. Checking water quality and treatment (Weekly)
Annual Actions: 1
Semi-Annual: 0
Monthly: 0
Weekly: 2
Daily: 0
Water Treatment Requirement: Yes
5Reference: https://www.thefreelibrary.com/Waterside+and+airside+economizers+design+considerations+for+data...-a0227975377
Number of Adiabatic Evaporative Cooling Systems3,4:
Note: The details of maintenance procedure and the frequency of steps have not been well defined for evaporative cooling.
The maintenance procedure can be assumed as follows:
1. Replacing/ cleaning cooling pads (Annually)
2. Checking cooling pads (Monthly)
3. Checking fan belts (Weekly)
4. Checking spray systems (Weekly)
5. Checking water quality and treatment: Yes
3,4References:
https://www.chemaqua.com/en-us/Blogs/how-do-adiabatic-cooling-systems-work
https://www.process-cooling.com/articles/89897-how-to-successfully-implement-evaporative-cooling
Note: For each cooling system the number and frequency of maintenance actions were listed below. A score was also assigned for each action (higher score means more severe action). Then for each cooling system, the overall maintenance score was calculated based on following formula. 𝑂𝑣𝑒𝑟𝑎𝑙𝑙 𝑀𝑎𝑖𝑛𝑡𝑒𝑛𝑎𝑛𝑐𝑒 𝑆𝑐𝑜𝑟𝑒=∑▒(𝑛𝑢𝑚𝑏𝑒𝑟 𝑜𝑓 𝑎𝑐𝑡𝑖𝑜𝑛×𝑎𝑐𝑡𝑖𝑜𝑛 𝑤𝑒𝑖𝑔ℎ𝑡)
Note: The higher maintenance score will negatively affect the rank of cooling system in MCDST.
Note: The maintenance actions for chillers, cooling tower, and air-side economizer are listed with details in the reference tabs; however, for evaporative cooling and water-side economizer there is no such a list of actions. So for pre-cooled air-cooled chiller, water-side economizer, and evaporative cooling systems I listed the actions based on available material and my thoughts. Please see the next sheets and cited references below.
1. Maintenance Actions Scores
Annual Actions: 5
Semi-Annual: 4
Monthly: 3
Weekly: 2
Daily: 1
Water Treatment Requirement: 10
Number of Maintenance Actions for a Chiller1:
Annual Actions: 10
Semi-Annual: 4
Monthly: 0
Weekly: 6
Daily: 3
Water Treatment Requirement: No
1Reference: https://www.energy.gov/sites/prod/files/2013/10/f3/omguide_complete.pdf
Number of Maintenance Actions for a Cooling Tower1:
Annual Actions: 3
Semi-Annual: 0
Monthly: 4
Weekly: 7
Daily: 3
Water Treatment Requirement: Yes
1Reference: https://www.energy.gov/sites/prod/files/2013/10/f3/omguide_complete.pdf
Number of Maintenance Actions for an Air-Side Economizer2:
Annual Actions: 1
Semi-Annual: 3
Monthly: 0
Weekly: 1
Daily: 0
Water Treatment Requirement: No
2Reference: https://www.pnnl.gov/projects/best-practices/air-side-economizers#Maintenance%20Checklist
Number of Pre-cooled Air-Cooled Chillers3,4:
Note: The details of maintenance procedure and the frequency of steps have not been well defined for Pre-cooled Air-Cooled Chillers.
The maintenance procedure can be assumed based on air-cooled chiller maintenance and evaporative cooling maintenance procedures.
1. Replacing/ cleaning cooling pads (Annually)
2. Checking cooling pads (Monthly)
3. Checking fan belts (Weekly)
4. Checking spray systems (Weekly)
5. Checking water quality and treatment: Yes, but not as severe as other systems
3,4References:
https://www.chemaqua.com/en-us/Blogs/how-do-adiabatic-cooling-systems-work
https://www.process-cooling.com/articles/89897-how-to-successfully-implement-evaporative-cooling
Number of Maintenance Actions for a Water-Side Economizer5:
Note: The details of maintenance procedure and the frequency of steps have not been well defined for WSE.
The maintenance procedure can be assumed as follows:
1. Checking heat exchanger for fouling/scaling using their approach temperature (weekly)
2. Cleaning heat exchangers as required (Depending on water quality may need to be down very frequently. In this case since we define a score for water treatment and quality check, the frequency of heat exchanger cleaning may be needed as annually
3. Checking water quality and treatment (Weekly)
Annual Actions: 1
Semi-Annual: 0
Monthly: 0
Weekly: 2
Daily: 0
Water Treatment Requirement: Yes
5Reference: https://www.thefreelibrary.com/Waterside+and+airside+economizers+design+considerations+for+data...-a0227975377
Number of Adiabatic Evaporative Cooling Systems3,4:
Note: The details of maintenance procedure and the frequency of steps have not been well defined for evaporative cooling.
The maintenance procedure can be assumed as follows:
1. Replacing/ cleaning cooling pads (Annually)
2. Checking cooling pads (Monthly)
3. Checking fan belts (Weekly)
4. Checking spray systems (Weekly)
5. Checking water quality and treatment: Yes
3,4References:
https://www.chemaqua.com/en-us/Blogs/how-do-adiabatic-cooling-systems-work
https://www.process-cooling.com/articles/89897-how-to-successfully-implement-evaporative-cooling
Action Score
Action Weight
Number of Actions

## MCDST-Values (3) (hidden)
|  | Parameters Weight |  |  |  | Normalized Performance Values (NPVs) |  |  |  | Weighted Normalized Values(WNVs) | [7 empty] | Ideal Worst Value (V-)
|  | 30% | 15% | 5% | 50%
Cooling System | Paramter Unit | Energy Use (MWh) | Onsite Water Use (acre-ft) | Source Water Use (acre-ft) | Reliability | NPV_Energy | NPV_Onsite Water | NPV_Source Water | NPV_Reliability | WNV_Energy | WNV_Onsite Water | WNV_Source Water | WNV_Reliability | V+_Energy | V+_Onsite Water | V+_Source Water | V+_Reliability | V-_Energy | V-_Onsite Water | V-_Source Water | V-_Reliability
Air-Cooled Chiller | MWh | 10740.2398 | 0 | 15.1506 | 1 | 0.6455 | 0 | 0.6455 | 0.51367 | 0.19365 | 0 | 0.032275 | 0.25683 | 0.064995 | 0 | 0.010833 | 0.25683 | 0.19365 | 0.14933 | 0.032275 | 0.17978
Air-Cooled Chiller+ ASE | MWh | 4727.4162 | 0 | 6.6687 | 0.7 | 0.28412 | 0 | 0.28412 | 0.35957 | 0.085236 | 0 | 0.014206 | 0.17978
Pre-Cooled-Air-Cooled Chiller | MWh | 9248.5852 | 7.2587 | 13.0464 | 1 | 0.55585 | 0.079338 | 0.55585 | 0.51367 | 0.16675 | 0.011901 | 0.027792 | 0.25683
Pre-Cooled-Air-Cooled Chiller +ASE | MWh | 3604.7818 | 4.6264 | 5.085 | 0.7 | 0.21665 | 0.050568 | 0.21665 | 0.35957 | 0.064995 | 0.0075852 | 0.010833 | 0.17978
Water-Cooled Chiller | MWh | 6373.0023 | 91.0842 | 8.99 | 0.9 | 0.38302 | 0.99556 | 0.38302 | 0.4623 | 0.11491 | 0.14933 | 0.019151 | 0.23115
Cooling System | Distanc from Ideal Best (S+) | Distanc from Ideal Worst (S-) | S++S- | Perfomance Score (PS) | Rank of Cooling Systems
Air-Cooled Chiller | 0.13043 | 0.16804 | 0.29847 | 0.56301 | 4
Air-Cooled Chiller+ ASE | 0.079736 | 0.18542 | 0.26516 | 0.69929 | 2
Pre-Cooled-Air-Cooled Chiller | 0.10385 | 0.1599 | 0.26375 | 0.60626 | 3
Pre-Cooled-Air-Cooled Chiller +ASE | 0.077422 | 0.19263 | 0.27005 | 0.7133 | 1
Water-Cooled Chiller | 0.15975 | 0.094927 | 0.25468 | 0.37273 | 5